## Slide 1: Energy from Wastewater Treatment Plants
D. Inman
April 2016

## Slide 2: Biogas from WWTP
16,000 facilities in the US
1500 have AD
1351 have AD without CHP
Facilities without AD installed are unlikely to install AD (EPA, 2011; Murray, 2014)
The primary driver to AD installation is solids handling (reduce tipping fee) and odor control.

## Slide 3: Biogas from WWTP specifics
Most biogas captured by AD is used for digester heating and is flared (EPA, 2011, Murray 2014).
WWTP options:
  Do nothing
  Install AD to reduce tipping fees and control odor
    Flare and heat digesters
    Install a reciprocating engine/micro turbine to generate CHP **this is only feasible for facilities with > 5 million gallons per day (MGD) inflow
    Capture and clean up the biogas to produce
      CHP
      PNG
      Make biofuel

## Slide 4: Biogas from WWTP-more specifics
Inflow (MGD) | Facilities with AD and w/o CHP | % with AD | Cumulative inflow (MGD)
1 – 5 | 845 | 37 | 5,124
5 – 10 | 230 | 51 | 3,188
10 - > 200 | 276 | 60 | 17,838
BTU = flow (MGD) x 1.18 x 10,000 ft3/MGD x 0.65 (CH4 factor) x 1,000 BTU/1 ft3 CH4

## Slide 5: Other information
Murray and the EPA have market potential estimates to 2040 – these may be handy to calibrate against.
Both assume new WWTPs will come online in response to population growth. These new WWTPs will have AD systems installed.
Both assume that if the WWTP does not have AD installed, it won’t install AD, so it does not enter the pool of potential contributors.
2040 projections for WWTP, from Murray 2014:
  1 – 5 MGD = 1002
  5 – 10 MGD = 273
  10 - > 200 = 331

## Slide 6: Misc…

## Slide 7: The WWTP Landscape
16,000 facilities in the US
1,500 have anaerobic digestion
104 facilities have CHP
Median energy used to treat wastewater is 10 k Btu/gallon/day, range (3 – 36)
Median utilization = 60%
Median inflow = 3 million gal day, range (0.2 to 74)
Estimated potential = 851 trillion Btu/yr

## Slide 8: Energy Options
Anaerobic digestion
  Biogas
    CHP
  CNG
    Vehicles
  PNG
    NG replacement
Thermal processes
  Incineration/co-combustion
    CHP
  Gasification
    Syngas
      CHP
      biofuels
    CNG
      Vehicles
    PNG
      NG replacement
  Pyrolysis
    Biofuel

## Slide 9
WWTP can use food wastes in their AD systems
Food waste has 3X more potential energy than the biosolids from the WWTP.
Slurry can have a maximum solids content of 15%
Mean municipal waste water solids content is 0.07%, half of which are organic.

## Slide 10: Wastewater chemistry
EOLSS - CHEMISTRY OF WASTEWATER
Table 8. Typical composition of untreated domestic wastewater. Values for chloride and sulfate should be increased by amount already present in the domestic water supply.
Adapted from Metcalf and Eddy (1991) Wastewater Engineering. Treatment Disposal Reuse, G. Tchobanoglous and F.L. Burton (Eds.), 1820 pp. New York: McGraw-Hill.
 |  | Concentration |  | 
Contaminants | Unit | Weak | Medium | Strong
Solids, total (TS) | mg L-1 | 350 | 720 | 1200
Dissolved, total (TDS) | mg L-1 | 250 | 500 | 850
Fixed | mg L-1 | 145 | 300 | 525
Volatile | mg L-1 | 105 | 200 | 325
Suspended solids (SS) | mg L-1 | 100 | 220 | 350
Fixed | mg L-1 | 20 | 55 | 75
Volatile | mg L-1 | 80 | 165 | 275
Settleable solids | mg L-1 | 5 | 10 | 20
BOD5 at 20° C | mg L-1 | 110 | 220 | 400
Total organic carbon (TOC) | mg L-1 | 80 | 160 | 290
Chemical oxygen demand (COD) | mg L-1 | 250 | 500 | 1000

## Slide 11: Technologies and energy use
Of the WWTP that have AD
  49 % goes to digester heating
  27 % goes to facility heating
  15 % goes to power generation
  8 % goes to drive machinery
  1 % goes to pipeline injection
Electricity technologies
  76 % internal combustion engine
  12 % microturbine
  7 % turbine
  5% fuel cell

## Slide 12: TEA Data
Inflow MM gal/day | # Facilities | Ft3 845per MGD | MM Btu/MGD | CHP cap Btu/MGD | Elec cap kW.MGD | Turbine elec $/kWh | SCFH gas per facility | conditioning unit | conditioning O&M
>200 | 7 | 10,000 | 1000 | 2.4 | 26 | $0.032 | 179,167 | $8,600,000 | $1,276,000
100 – 200 | 13 | 10,000 | 1000 | 2.4 | 26 | $0.040 | 66,538 | $3,800,000 | $315,100
75 – 100 | 17 | 10,000 | 1000 | 2.4 | 26 | $0.040 | 36,005 | $3,000,000 | $132,000
50 – 75 | 17 | 10,000 | 1000 | 2.4 | 26 | $0.040 | 26,422 | $3,000,000 | $132,000
20 – 50 | 82 | 10,000 | 1000 | 2.4 | 26 | $0.051 | 12,658 | $2,270,000 | $86,600
10 – 20 | 140 | 10,000 | 1000 | 2.4 | 26 | $0.051 | 5,830 | $845,000 | $36,535
5 - 10 | 230 | 10,000 | 1000 | 2.4 | 26 | $0.060 | 2,953 | $845,000 | $36,535
1 - 5 | 845 | 10,000 | 1000 | 2.4 | 26 | $0.064 | 1,027 | $845,000 | $36,535

## Slide 13: Cap and Op Ex
AD System
  Capital $561/ton
  O&M costs $48/ton
  Discount rate 10%
  Interest rate 7%
  Debt payment 15 yr
Data from K. Moriarty, 2013.

## Slide 14: Cap and Op Ex
HTL to biocrude system
  Installed capital $28,000,000
  Total capital $54,000,000
  Loan rate 8%
  Loan term 10 yr
  Inflow rate 92 tons per day
  Hours per year 7,920
  Op costs 5,500,000