## Slide 1
Facility influx
biosolids
biogas
biocrude
CHP
PNG
CNG
HC via FT
HC via
waste for disposal
waste for disposal
19.2 x92.4% mmBTU sludge2
MG
12.0 MMBTU biocrude1
MG
10.1 MMBTU biogas
MG
57.2% energy yield
62.6% energy yield
100 – (62.6*0.924) = 42.2%
Disposal required as compared to no WTE
100 – (57*0.924) = 47.3%
Disposal required as compared to no WTE
AD
HTL
92.4% ash-free1
93% conversion efficiency1
58.2% energy yield
29--45% conversion efficiency3 from biogas
16.5-25.6% energy yield
56-89% conversion efficiency
31.9%-50.7% energy yield
45.9%-54.6% conversion efficiency
26.2%-31.1% energy yield
Yield Calculations for WWTP Model
Values in black are from documented data sources
Values in blue are calculated
Values in red need to be found or verified
Data Sources:
1 PNNL. 2016. HTL Design Report.
2 PNNL. 2016. HTL Design Report.
Converted from 9,589 Btu/lb
3 35% is reported in EPA. 2011.
Market Opportunities for Biogas
Recovery Systems at U.S. Livestock Facilities
Notes: CNG: EIA compressed to 200-248bar, local distribution system (200 psig or 14 bar)
PNG: compressed to 200-1500 psi
10,000 scf biogas per MG WW, equivalent to 10.7 GJ/MG and 10.1 MMBTU/MG

## Slide 2
Facility influx
biosolids
biogas
biocrude
CHP
PNG
CNG
HC via FT
HC fuel
waste for disposal
waste for disposal
19.2 mmBTU sludge2
Dry ton
12 mmBTU biocrude1
MG
10.4 mmBTU biogas
MG
54.3% energy yield
62.6% energy yield
100 – (62.6*0.924) = 42.16%
Disposal required as compared to no WTE
7.61 + 0.1*(100-54.3) = 12.17%
Disposal required as compared to no WTE
AD
HTL
92.4% ash-free1
93% conversion efficiency1
58.22% energy yield
29% conversion efficiency3
15.75% energy yield
56% conversion efficiency
30.41% energy yield
?% conversion efficiency
?% energy yield
56% conversion efficiency
30.41% energy yield
Yield Calculations for WWTP Model
Values in black are from documented data sources
Values in blue are calculated
Values in red need to be found or verified
Data Sources:
1 PNNL. 2016. HTL Design Report.
2 PNNL. 2016. HTL Design Report.
Converted from 9,589 Btu/lb
3 35% is reported in EPA. 2011.
Market Opportunities for Biogas
Recovery Systems at U.S. Livestock Facilities
OLD DATA